## Sheet1
LIST OF PARAMETERS
No. | Item | Description | Type | Format | Comment
1 | N1 | Motor speed | REAL | 0~999999 | Unit : rpm
2 | Wm | Motor input power | REAL | 0~9999.9 | Unit : kW
3 | Pd | Discharge pressure | REAL | 0~9999.99 | Unit : kgf/㎠ / kPa / PSI
4 | dPi | Inlet filter DP | REAL | 0~99.9999 | Unit : kgf/㎠ / kPa / PSI
5 | Ts | Suction temperature | REAL | 0~9999.99 | Unit : ℃ / ℉
6 | Td | Discharge temperature | REAL | 0~9999.99 | Unit : ℃ / ℉
7 | Tm | Motor temperature | REAL | 0~9999.99 | Unit : ℃ / ℉
8 | Tb | Bearing temperature | REAL | 0~9999.99 | Unit : ℃ / ℉
9 | Xm | Motor vibration | REAL | 0~999.99 | Unit : ㎛ / mil
10 | Q | Suction air flow | REAL | 0~99999.9 | Unit : ㎥/min / Ｎ㎥/min / Ｎ㎥/min(*) / CFM / SCFM
11 | Nc_max | Max speed based on Suction temperature | REAL | 0~999999 | Unit : rpm / mg/ℓ
12 | B_status | Blower status | BINARY | 0~1000000
13 | Nscm | Max speed limit condition | BINARY | 0~100
14 | Ctrl_mode | Control mode status | BINARY | 0~1000
15 | Site_mode | Remote mode status | BINARY | 0~1000
16 | Surge_mode | Protection mode status | BINARY | 0~1000
17 | T_run_min | Total running time | INT | 0~60 | Unit : Minute
18 | T_run_hour | Total running time | DINT | 0~4294967295 | Unit : Hour
19 | C_run_hour | Current running time | DINT | 0~4294967295 | Unit : Hour
20 | F_history_order | Fault history number | INT | 0~25
21 | F_history_code | Fault history code | INT | 0~9999
22 | F_history_value | Fault history value | REAL | 0~99999.999
23 | F_history_year | Fault history time | INT | 0~99 | Unit : Year
24 | F_history_month | Fault history time | INT | 0~12 | Unit : Month
25 | F_history_day | Fault history time | INT | 0~31 | Unit : Day
26 | F_history_hour | Fault history time | INT | 0~24 | Unit : Hour
27 | F_history_min | Fault history time | INT | 0~60 | Unit : Min
28 | N1_max | Motor speed limit | REAL | 0~999999 | Unit : rpm
29 | Pi_max | Inlet filter DP limit | REAL | 0~999.999 | Unit : kgf/㎠ / kPa / PSI
30 | Xm_max | Moto vibration limit | REAL | 0~999.99 | Unit : ㎛ / mil
31 | Pd_max | Discharge pressure limit | REAL | 0~9999.99 | Unit : kgf/㎠ / kPa / PSI
32 | Ts_max | Suction temperature limit | REAL | 0~9999.99 | Unit : ℃ / ℉
33 | Td_max | Discharge temperature limit | REAL | 0~9999.99 | Unit : ℃ / ℉
34 | Tm_max | Motor temperature limit | REAL | 0~9999.99 | Unit : ℃ / ℉
35 | Tb_max | Bearing temperature limit | REAL | 0~9999.99 | Unit : ℃ / ℉
36 | Wm_max | Motor input power limit | REAL | 0~9999.9 | Unit : kW
37 | Ox | D.O(Dissolved oxygen) | REAL | 0~999.9 | Unit : rpm / mg/ℓ
38 | Warning_code | Warning code | INT | 0~9999
39 | Fault_code | Fault code | INT | 0~9999
40 | Heart_bit | Communication check bit | BIT | 0~1
41 | N1_min | Minimum speed | REAL | 0~999999.9 | Unit : rpm
42 | Input_current | Input current (Approx.) | REAL | 0~9999.99 | Unit : A
LIST OF COMMANDS
No. | Item | Description | Type | Format | Comment
46 | Target | Percent of target value | REAL | 0~100.0 | Unit : %
47 | Start_stop | Start / stop command | INT | 1234 / 4321 | 1234 : Start, 4321 : Stop